## Slide 1
👤 Operator · wireless · upstream
⚙ Substation Edge Compute (this appliance)
🏢 Station
🔀 Process / bay
⚡ Switchyard + sensors
Upstream (out of substation)
Wireless / remote access (phone connectivity)
Operator surfaces
Safety Module daughtercard
x86 HOST · Cloud Hypervisor microVMs
Inputs (4 channels)
Station level (control house)
Bay level IEDs
Process level (MUs + PIUs)
Physical security + perimeter
Asset-condition sensors (PHY · APP)
Switchyard (outdoor)
MV side · 69 kV
HV side · 230 kV
secondary
CT/VT sec
aux + trip coil
OLTC + cooling
GOOSE trip
GOOSE trip
GOOSE trip
PTP master
PTP master
power gate
SPAN / mirror
SPAN / mirror
SMS / push
WAN backhaul
audit egress
mode events · SSE
telemetry + control
audit egress (batched)
handshake → INVESTIGATION
engineering laptop
local service tool
redundant WAN
230 kV in
Line bay SA·DS·CB·CT·VT·ES
HV bus double bus + coupler
Xfmr bay CT/CB (HV)
Power xfmr 230/69 kV · 100 MVA · OLTC
LV side CB/CT (LV)
MV bus double bus + coupler
Feeder bay CT·CB·DS
69 kV out → distribution
DGA oil gases
PD UHF+acoustic+HFCT
Bushing tap C · tan δ
Vibration / acoustic
Top-oil + winding RTD · FBG
OLTC monitor
SF6 density
Station battery V · IR · ripple
Ctrl-house env T · RH · door
IP dome / PTZ PoE · ONVIF/RTSP
Thermal IR cam ONVIF + GenICam
Fence-line intrusion fiber / piezo cable
Gate access reader RFID · OSDP (RS-485)
Door/window + motion PIR · tamper
Local NVR / VMS H.264/H.265
MU line SV 9-2LE + GOOSE
MU xfmr HV + LV SV
MU bus 3φ V SV
MU feeder SV + GOOSE
PIU line CB/DS/ES + trip
PIU xfmr OLTC · cooling
PIU feeder
Process bus L2 Ethernet · PRP / HSR · SV (9-2 LE) + GOOSE + PTP (9-3)
21 line distance
87T xfmr diff
87B busbar diff
50/51/51N OC / EF
Bay controller interlocking · SOE
Station bus Ethernet (PRP) · MMS + GOOSE + PTP
Station HMI
Station ctrl logic / seq
SCADA gateway DNP3 / 60870-5-104
Engineering WS SCL·CID·IID
PTP grandmaster GPS-disciplined 1588v2 / 9-3
Remote-access router corp WAN · jump
Process-bus tap SPAN (RO) · SV + GOOSE
Station-bus tap SPAN (RO) · MMS + SOE + GOOSE
Asset-cond aggregator RS-485 · 4-20 mA+HART · Modbus TCP · DNP3 · 61850 MMS · SNMP
Security aggregator RTSP/ONVIF · OSDP · BACnet MS/TP · dry contacts · NVR API
mcp_edge
llm_orchestrator
frontier_llm_api
seal_authority « stub »
GPU Platform · frontier LLM · PCIe
dsp_frontend
token_emitter
grammar_parser
anomaly_detector
capsule_store
voice_tag
SME workstation PyQt6 UI State Viewer · bus emulator · LLM loop · session console
Cellular modem 4G LTE / 5G NSA APN + IPsec VPN MQTT / HTTPS uplink
Wi-Fi AP 802.11ac · WPA2-Ent (engineering only)
Bluetooth LE field-engineer tool (pairing-gated)
SME phone notify SMS / push call-out
Utility control centre EMS / DMS / OMS DNP3 / 60870-5-104
Asset-mgmt portal batch · NERC CIP
Remote SME (on-call) secure tunnel
Read-only by design. Passive listener on both buses (SPAN/mirror); never publishes GOOSE, never commands MMS, never trips a breaker. Surfaces evidence to the SME.
Seal contract gates GPU power. SEALED ⇄ AWAITING_SME ⇄ INVESTIGATION is the SME flow. GPU unpowered in SEALED.
One time domain. The substation PTP grandmaster disciplines both buses AND the edge compute's signal-plane clock (origin_ns sealed at ingest).
Physical-security feeds are read-only too — capture + correlate, never command. Camera + PD cross-correlation is a target Stage 7e+ use case.