## Slide 1
⇨ to diagram 16b (SEC appliance)
🏢 Station level (control house)
Bay level (protection + control IEDs)
🔀 Process level (MUs + PIUs)
Asset-condition + physical-security sensors
⚡ Switchyard (outdoor)
Physical security + perimeter
Asset-condition (PHY · APP)
MV side · 69 kV
HV side · 230 kV
secondary
CT/VT sec
aux + trip coil
OLTC + cooling
GOOSE trip
GOOSE trip
GOOSE trip
PTP master
PTP master
SPAN / mirror
SPAN / mirror
230 kV in
Line bay SA·DS·CB·CT·VT·ES
HV bus double bus + coupler
Xfmr bay CT/CB (HV)
Power xfmr 230/69 kV · 100 MVA · OLTC
LV side CB/CT (LV)
MV bus double bus + coupler
Feeder bay CT·CB·DS
69 kV out → distribution
DGA oil gases
PD UHF+acoustic+HFCT
Bushing tap C · tan δ
Vibration / acoustic
Top-oil + winding RTD · FBG
OLTC monitor
SF6 density
Station battery V · IR · ripple
Ctrl-house env T · RH · door
IP dome / PTZ PoE · ONVIF / RTSP
Thermal IR cam ONVIF + GenICam
Fence-line intrusion fiber / piezo cable
Gate access reader RFID · OSDP (RS-485)
Door / window + motion PIR · tamper
Local NVR / VMS H.264 / H.265 record
MU line SV 9-2LE + GOOSE
MU xfmr HV + LV SV
MU bus 3φ V SV
MU feeder SV + GOOSE
PIU line CB/DS/ES + trip
PIU xfmr OLTC · cooling
PIU feeder
Process bus · L2 multicast Ethernet · PRP / HSR · SV (9-2 LE) + GOOSE + PTP (9-3)
21 line distance
87T xfmr diff
87B busbar diff
50/51/51N OC / EF
Bay controller interlocking · SOE
Station bus · Ethernet (PRP) · IEC 61850-8-1 MMS + GOOSE · PTP (9-3)
Station HMI
Station ctrl logic / seq
SCADA gateway DNP3 / 60870-5-104
Engineering WS SCL · CID · IID
PTP grandmaster GPS-disciplined 1588v2 / 9-3
Remote-access router corp WAN · jump
"SPAN / mirror (process bus) → 16b · tap_pbus"
"SPAN / mirror (station bus) → 16b · tap_sbus"
"Asset-condition feeds RS-485 · 4-20 mA+HART · Modbus TCP · DNP3 · 61850 MMS · SNMP → 16b · acm_in"
"Physical-security feeds RTSP/ONVIF · OSDP · BACnet MS/TP · dry contacts · NVR API → 16b · sec_in"
"SCADA upstream DNP3 / 60870-5-104 → 16b · control centre"
"Remote-access corp WAN / jump host → 16b · remote SME"
"PTP master · 1588v2 → 16b · signal-plane clock (origin_ns ingest)"
The signal-tier appliance (16b) is a <b>passive listener</b>. It receives SPAN/mirror copies of the buses, slow-telemetry from the sensor aggregators, and read-only context from SCADA; it never publishes GOOSE, never commands MMS, never trips a CB.
One time domain. The substation PTP grandmaster disciplines both buses AND the appliance's signal-plane clock (16b · origin_ns at ingest).